Text for specification

Description
SECUR^®Panel
chave seccionadora para fusíveis D0 até 63 A
com LED
1P

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
VDE

Electrical data
Corrente de medição (IEC):	63 A
Tensão de medição (IEC) AC:	400 V
Tensão de medição (IEC) DC:	65 V

AC-22B (400V)

 DC-22B (65 V)

power dissipation at full load of the item:	2,6 W

Tensão nominal de isolamento:	500 V
Tensão suportável nominal de impulso Uimp:	6 kV

for fuse links and gauge rings as per DIN VDE 0636-3 IEC / HD 60269-3
utilisation category as per VDE 0638: AC-22 (400V)

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard.

There is a transfer of the potential from the busbars, through the LED units, to the terminals  when the fuse links are removed and the switching mechanismn is closed. 

Miscellaneous 
Double function terminal
any feed direction
captive fuse-carrier
sealable operation

Brand 
Woehner or equivalent

Nº da peça
31556000A