Text for specification

Description
QUADRON^®60Classic Speed
chave seccionadora sob carga 3 polos
prensa-cabo, conexão inferior
160 A
60Classic

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB)

Electrical data
Corrente de medição (IEC):	160 A
Tensão de medição (IEC) AC:	690 V

AC-23B (690V/125A)
AC-23A (500V/125A)
AC-22A (690V/160A)

DC specifications: 2 current paths (L1,L3) in series
DC-22B (220V/125A) 

power dissipation at full load of the item:	41,8 W

Tensão nominal de isolamento:	800 V
Tensão suportável nominal de impulso Uimp:	8 kV

rated short-circuit making capacity 7kA (690V AC)

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

When several devices are used side-by-side in continuous operation, the rated load factor specified in VDE 0660 Part 500 / EN 60 439-1, Table 1, must be observed.

System component: degree of protection IP20 at front as per DIN EN 60529, degree of protection near terminal depends on installation; shock protection as per DIN EN 50274
adapter module: front side degree of protection IP20 as per DIN EN 60529 (finger-safe)

pontos terminais
Box terminal:
1.5 -70mm² flexible cables, directly or with wire-end ferrules*, depending on contour of the insulated lead 95mm² could be connectable 
1.5 - 10mm² solid round
16 - 70mm² stranded round 
2x10mm², 2x16mm² and 2x25mm² flexible with wire-end ferrules, identical cables placed side by side, crimping square 
2x10 - 2x35mm² flexible, identical cables placed side by side square

lam. Cu. 9-13 mm wide 
Terminal space 13mm x 13mm

(*flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Miscellaneous 
With spring-controlled switch mechanism for frequent switching as per utilisation category &quot;A&quot;
Lockable in neutral position with up to 3 padlocks
FLAG indicator shows the switch setting of double interrupting main contacts
Can be used as a mains disconnector as per IEC / EN 60204-1 (main switch) 
Main switch only in combination with AC-23A/B
AC-23B (690V/125A), AC-23A (500V/125A)

CrossLink® adapter technology
Simple and safe clicking into place and making contact
Busbar supports can be mounted above each other for flat busbars

Compact dimensions (106mm wide)

Brand 
Woehner or equivalent

Nº da peça
33540000