Text for specification

Description
QUADRON®185Power
chave seccionadora de fusível vertical 160 A
Tamanho 00, comutável 3 polos, com monitorização do fusível
high version with box terminal 70 mm²
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Standards
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Approvals
IEC (CB), CCC

Electrical data
Corrente de medição (IEC):	160 A
Tensão de medição (IEC) AC:	400 V

AC-23B 160A/400V
AC-22B 160A/500V 

power dissipation at full load of the item:	28,0 W

Tensão nominal de isolamento:	400 V
Tensão suportável nominal de impulso Uimp:	4 kV

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

Degree of protection IP20 at front, degree of protection near terminal depends on installation

pontos terminais
Box terminal:
1,5 -70mm² flexible cables, directly or with wire-end ferrules*, depending on contour of the insulated lead 95mm² could be connectable
1,5 -10mm² solid round
16 -70mm² stranded round
2x10mm², 2x16mm² and 2x25mm² flexible with wire-end ferrules, identical cables placed side by side, crimping square
2x 10-35mm² flexible identical cables placed side by side

lam. Cu. 9-13 mm wide
terminal space 13mm x 13mm

(*flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Miscellaneous 
Self-closing inspection holes are available in the cover.
Cover can be locked when closed.

Brand 
Woehner or equivalent

Nº da peça
33771000A