Text for specification

Описание 
CRITO^®60Classic
Комплект для подсоединения, 4-полюсный, без крышки
95 -  300 mm², AWG 3/0 - 600 MCM
60Classic

Стандарты
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Сертификация
UL

Электрические данные
Номинальный ток (IEC):	500 A
номинальное напряжение (IEC) AC:	800 В

номинальный ток (UL):	420 A
номинальное напряжение (UL) AC:	600 В
токовая нагрузка (IEC) макс.:	560 A
макс. напряжение IEC AC:	1000 В
макс. напряжение IEC DC:	1500 В

номинальный выдерживаемый пиковый ток I  _pk  макс.:	50,3 кА

SCCR: 65 kA with any DIVQ/7 circuit breaker 400 A / 480 V AC, 35 kA with any DIVQ/7 circuit breaker 400 A / 600 V AC, 200 kA with fuse JDDZ Class J 600 A / 600 V AC, 200 kA with JDDZ fuse Class L 800 A / 600 V AC, 100 kA with JDDZ fuse Class L 1200 A / 600 V AC 

Особенности клеммной техники
Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

Свойства материала
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200

Terminals: 	galvanised steel, chromited screw: 	hexagon socket screw, galvanised, chromited, thrust piece 	brass, nickel-plated

Brand 
Woehner or equivalent

Арт.
01147000