Text for specification

Описание 
CRITO®30Compact
Подсоединительная клеммная платформа, 3-полюсная
35 - 150 mm², AWG 2 - 300 MCM,  lam. Cu. 15 - 20 x 5 - 10
30Compact 3P

Стандарты
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Сертификация
UL

Электрические данные
Номинальный ток (IEC):	275 A
номинальное напряжение (IEC) AC:	690 В

номинальный ток (UL):	285 A
номинальное напряжение (UL) AC:	600 В
токовая нагрузка (IEC) макс.:	480 A
макс. напряжение IEC AC:	1000 В
макс. напряжение IEC DC:	1500 В

номинальный выдерживаемый пиковый ток I  pk  макс.:	45,9 кА

SCCR:	18 кА

Особенности клеммной техники
for applications acc. to IEC / EN :
35 - 150 mm² stranded round cables and stranded sectored cables
flexible cables, directly or with wire-end ferrule
(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

also for the connection of lam. Cu up to 20x10 

for applications acc. to UL / CSA :
only Cu cables Class B acc. to UL 486E
35 - 150 mm² / AWG 2 - MCM 300

Свойства материала
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200

Terminals: 	galvanised steel, chromited screw: 	hexagon socket screw M8 x 37, thrust piece: 	brass, nickel-plated

Miscellaneous 
Terminals with captive clamping screws
Conductor can be overlapped
Indication of nominal cross-section and tightening torque noted on the terminals.

Brand 
Woehner or equivalent

Арт.
01165000