Text for specification

Описание 
CRITO^®185Power
Соединительный модуль
3-полюсный
Для 3 кабельных наконечников 300 мм², для 4 наконечников 240 мм² или гибк. шины 80 х 10
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Стандарты
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Электрические данные
Номинальный ток (IEC):	1 400 A
номинальное напряжение (IEC) AC:	690 В

рассеиваемая мощность при номинальном непрерывном токе устройства:	550,0 Вт
токовая нагрузка (IEC) макс.:	1 400 A
макс. напряжение IEC AC:	1000 В
макс. напряжение IEC DC:	1500 В

номинальный выдерживаемый пиковый ток I  _pk  макс.:	87,4 кА

a current carrying capacity of 1400A was proved, when connected with 4 cables 240mm² (direct screw connection of the connection rail to the busbar system)

the current carrying capacity is reduced to 1200A when the connection rail is combined with the terminal clamps 33 738 or 33 740

it is possible to connect up to 4 cable lugs 300mm² acc. to DIN 46235 

Свойства материала
Main body:
	temperature stability 130°C,
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Shock protection cover:
	temperature stability 125°C,
	 self-extinguishing in acc. to UL 94,
	 creepage resistance CTI 600,
	 halogen-free 

Brand 
Woehner or equivalent

Арт.
01439000A