Text for specification

Описание 
QUADRON^®60Classic
Держатель NH предохранителей 160 A
Рамная клемма
Типоразмер 00 / 3 полюса
60Classic

Стандарты
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Сертификация
IEC (CB), VDE, CCC

Электрические данные
Номинальный ток (IEC):	160 A
номинальное напряжение (IEC) AC:	690 В
номинальное напряжение (IEC) DC:	440 В

рассеиваемая мощность при номинальном непрерывном токе устройства:	13,0 Вт
номинальное импульсное напряжение U  _imp :	6 kV
макс. напряжение IEC AC:	800 В
макс. напряжение IEC DC:	800 В
устойчивость к короткому замыканию при защите предохранителями:	50 кА

Adapter module: front side degree of protection IP20 as per DIN EN 60529 (finger-safe)

Особенности клеммной техники
Box terminal:
1.5 - 70 mm² flexible cables, directly or with wire-end ferrules*, depending on contour of the lead 95 mm² could be connectable 
1.5 - 10 mm² solid round
16 - 70 mm² stranded round 
2x 10 mm², 2x 16 mm² and 2x 25 mm² flexible with wire-end ferrules, identical cables placed side by side, crimping square 
2x 10 - 35 mm² flexible identical cables placed side by side

lam. Cu. 9 - 13 mm wide 
terminal space 13 mm x 13 mm

(*flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Свойства материала
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 
Adapter plate:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Shock protection cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200

Miscellaneous 
CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom
Simple and safe clicking into place and making contact
Safe connection through shock protection split into two
Busbar supports for flat busbars can be mounted above each other

Brand 
Woehner or equivalent

Арт.
03199000