Text for specification

Описание 
QUADRON®Panel
Держатель NH предохранителей 250 A, панельный монтаж, для солн. энерг.
Подсоединение входа винтовое М10, выхода - к шине 2 х 30 х 10
Типоразмер 1XL / 1 полюс, с защитой от прикосновения

Стандарты
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Сертификация
UL

Электрические данные
Номинальный ток (IEC):	250 A
номинальное напряжение (IEC) AC:	1000 В
номинальное напряжение (IEC) DC:	1500 В

номинальный ток (UL):	250 A
номинальное напряжение (UL) DC:	1500 В

рассеиваемая мощность при номинальном непрерывном токе устройства:	5,5 Вт
номинальное импульсное напряжение U  imp :	6 kV
устойчивость к короткому замыканию при защите предохранителями:	50 кА

SCCR:	15 кА

for fuse links IEC 60269-6

Свойства материала
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 
Connecting screws:
	screw M10, galvanized, chromized
Shock protection cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
For one or two internal busbars 30x10mm.
Busbar fully shock protected by the contact cover.
The shock protection is split into 2.

Brand 
Woehner or equivalent

Арт.
03289000