Text for specification

Описание 
AMBUS^®Panel
Держатель цилиндрических предохранителей
14x51 / 1P
50 A / 690 V

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Сертификация
IEC (CB), CSA, UL, CCC

Электрические данные
Номинальный ток (IEC):	50 A
номинальное напряжение (IEC) AC:	690 В

номинальный ток (UL):	50 A
номинальное напряжение (UL) AC:	600 В
номинальное напряжение (UL) DC:	600 В

рассеиваемая мощность при номинальном непрерывном токе устройства:	0,9 Вт

номинальное напряжение изоляции U  _i  AC:	800 В
номинальное импульсное напряжение U  _imp :	6 kV

SCCR:	100 кА

for fuse links as per IEC / EN 60269-2 with permitted rated power dissipations
up to max. 5W for gG/gL 
up to max. 3W for aM

Особенности клеммной техники
box terminal :
1,5 - 35 mm² / AWG 14 - AWG 2 
flexible cables, directly or with wire-end ferrule
Md 2,5 - 3,0 Nm / 22 - 26 lb.in.

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Свойства материала
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Fuse-carrier:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
	
Connecting screws:
	screw +/- (PZ2), galvanized, chromized 

Miscellaneous 
large clamping range
 holder for label

Brand 
Woehner or equivalent

Арт.
31115000