Text for specification

Описание 
SECUR^®60Classic PowerLiner
Крышка для держателя D-предохранителей
Для предохранителей D01 and D02
E18 / 63 A / 3 полюса
60Classic

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Сертификация
VDE, CCC

Электрические данные
Номинальный ток (IEC):	63 A
номинальное напряжение (IEC) AC:	400 В
номинальное напряжение (IEC) DC:	110 В

AC-23A (400 В)

DC-21B (48V) 1 pole
DC-21B (110V) 2 poles

рассеиваемая мощность при номинальном непрерывном токе устройства:	10,5 Вт

номинальное напряжение изоляции U  _i  AC:	500 В
номинальное импульсное напряжение U  _imp :	6 kV

for fuse links and gauge rings as per DIN VDE 0636-3 IEC / HD 60269-3
utilisation category as per VDE 0638: AC22

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard. 

Особенности клеммной техники
frame terminal:
Cu 1,5 - 6 mm² round solid
Cu 1,5 - 16 mm² flexible with or without ferrule

Свойства материала
Body:
	temperature stability 140°C,
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 225,
	silicon-free, halogen-free
Handle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Fuse-carrier:
	temperature stability 150°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 125,
	halogen-free
Cover:
	temperature stability 125°C,
	fire behaviour UL 94 HB,
	creepage resistance CTI 200,
	halogen-free 
Connecting screws:
	screw +/- (PZ2), galvanized, chromized 

Brand 
Woehner or equivalent

Арт.
31158000