Text for specification

Описание 
AMBUS®Panel
Держатель цилиндрических предохранителей, с контрольным доп. контактом
22 x 58 / 3P
100 A / 690 V

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Сертификация
CSA, UL, CCC

Электрические данные
Номинальный ток (IEC):	100 A
номинальное напряжение (IEC) AC:	690 В

номинальный ток (UL):	80 A
номинальное напряжение (UL) AC:	600 В
номинальное напряжение (UL) DC:	600 В

рассеиваемая мощность при номинальном непрерывном токе устройства:	10,5 Вт

номинальное напряжение изоляции U  i  AC:	800 В
номинальное импульсное напряжение U  imp :	6 kV

SCCR:	100 кА

for fuse links with striker as per IEC / EN 60269-2 with permitted rated power dissipationsup to max. 9.5W for gG/gL up to max. 7W for aMup to max. 11W for aR/gR at max. 80A pilot switch 1 changeover switch 250V AC (5A), 30V DC (4A)

Особенности клеммной техники
box terminal :
4 - 50 mm² / AWG 10 - AWG 1/0 
flexible cables, directly or with wire-end ferrule
Md 3,5 - 4,0 Nm / 31 - 35 lb.in.

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Свойства материала
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Fuse-carrier:
	temperature stability 140°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Connecting screws:
	screw +/- (PZ2), galvanized, chromized 

Miscellaneous 
large clamping range

Brand 
Woehner or equivalent

Арт.
31943000