Text for specification

Описание 
AMBUS®60Classic
Держатель предохранителей Class J для установки на шины , подсоединение снизу
Для предохранителей Class J 35 - 60 A (27x60), c LED
3-полюсный, изделие всборе на шинном адаптере
60Classic

Стандарты
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system H

Сертификация
CSA, UL

Электрические данные

номинальный ток (UL):	60 A
номинальное напряжение (UL) AC:	600 В
номинальное напряжение (UL) DC:	600 В

рассеиваемая мощность при номинальном непрерывном токе устройства:	10,7 Вт

SCCR:	100 кА

Особенности клеммной техники
for applications acc. to IEC / EN :
1 wire : Cu 6 - 50 mm², Md 3,5 - 4,0 Nm / 31 - 35 lb.in.
2 wires (of same cross-section) : Cu 6 - 16 mm², Md 3,5 - 4,0 Nm / 31 - 35 lb.in.
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)

for applications acc. to UL / CSA :
only Cu cables acc. to UL 486E
1 wire : AWG 14 - AWG 1, Class C, Md 4,0 Nm / 35 lb.in.
2 wires (of identical cross-section) :  AWG 14 - AWG 6, Class C, Md 4,0 Nm / 35 lb.in.

Свойства материала
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Adapter plate:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Fuse-carrier:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
	
Connecting screws:
	screw +/- (PZ2), galvanized, chromized 

Brand 
Woehner or equivalent

Арт.
31970000