Text for specification

Описание 
EQUES®185Power
Шинный адаптер 1400 A
300 x 652, подсоединение снизу, зажим хомутом, изменена фаза
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Стандарты
IEC 61439-1:2011

Сертификация
UL

Электрические данные
Номинальный ток (IEC):	1 400 A
номинальное напряжение (IEC) AC:	690 В
номинальное напряжение (IEC) DC:	800 В

номинальный ток (UL):	1 200 A
номинальное напряжение (UL) AC:	1000 В

рассеиваемая мощность при номинальном непрерывном токе устройства:	417,0 Вт

номинальное напряжение изоляции U  i  AC:	1000 В
номинальное импульсное напряжение U  imp :	12 kV

номинальный выдерживаемый пиковый ток I  pk  макс.:	106 кА

mit Schneider Electric NS1600 bis 1400A einsetzbar!

Brand 
Woehner or equivalent

Арт.
32718000A