Text for specification

Описание 
QUADRON^®60Classic
Выключатель-разъединитель с предохранителями NH типоразмер 2, 400 A, шинный монтаж
Винт М10
60Classic

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Сертификация
IEC (CB), UL, CCC

Электрические данные
Номинальный ток (IEC):	400 A
номинальное напряжение (IEC) AC:	690 В
номинальное напряжение (IEC) DC:	250 В

номинальный ток (UL):	400 A
номинальное напряжение (UL) AC:	600 В

AC-23B (400V)
AC-22B (500 V)
AC-21B (500 V)

рассеиваемая мощность при номинальном непрерывном токе устройства:	45,0 Вт

номинальное напряжение изоляции U  _i  AC:	690 В
номинальное импульсное напряжение U  _imp :	6 kV
макс. напряжение IEC AC:	725 В
макс. напряжение IEC DC:	262 В

SCCR:	100 кА

for fuse links IEC 60269-2-1 (I) / DIN VDE 0636-201 size 2 up to 34W power dissipation, with grip lugs under voltage

Schutzart IP30 frontseitig, im Anschlussbereich vom Einbau abhängig

Elektronische Sicherungsüberwachung:
- Zur Erkennung von Sicherungsausfällen mit Bemessungsspannung AC 100V bis AC 690V
- Keine Hilfsenergie erforderlich; Versorgung über Netzspannung
- Hilfskontakte potentialfrei
- LED- Blinkmelder (rot/grün)
- Testtaster
- Weitere Informationen unter Downloads / Datenblatt

Особенности клеммной техники
Accessories:
Clamp connection:  Cu 120-240mm² s(r), f+AE; lam. Cu 21x1-14; 6-8Nm torque
single wedge clamp terminal: Cu, Al* 120-240mm² s(r), s(s), f, f+AE; 6-8 Nm torque
double wedge clamp terminal: Cu  2x 70-120mm² s(r), s(s), f+AE;  6-8Nm torque

*Connections are not maintenance-free if aluminium conductors are used.

Свойства материала
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Shock protection cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Handle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Adapter plate:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 
Connecting screws:
	screw M10, galvanized, chromized

Miscellaneous 
Disconnectors are equipped with arc chambers.
The shock protection is split into 2 for safe connection of the conductors.

Brand 
Woehner or equivalent

Арт.
33326000