Text for specification

Описание 
CAPUS^®Panel
выключатель-разъединитель нагрузки 3-полюсный
Винт M12, ручка серая
800 A

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Сертификация
IEC (CB)

Электрические данные
Номинальный ток (IEC):	800 A
номинальное напряжение (IEC) AC:	500 В

AC-23B (500V)
AC-22B (500V)
AC-21B (500V)

рассеиваемая мощность при номинальном непрерывном токе устройства:	169,0 Вт

номинальное напряжение изоляции U  _i  AC:	1000 В
номинальное импульсное напряжение U  _imp :	12 kV
номинальная включающая способность:	40 кА

Mechanical lifespan (switching operations) 2500
rated short-circuit making capacity 40kA

conv. therm. current in housing
800A, horizontal installation (adjacent poles) encapsulated 756 x 378 x 482mm
800A, vertical installation (poles beneath each other) encapsulated 600 x 600 x 400mm

Shock protection at front with terminal space cover IP40

Особенности клеммной техники
screw M12 :
Md 36 - 44 Nm

Miscellaneous 
double-breaking main contacts, 
visible separation sections, 
user-independent switching, 
assembly and connection material contained in scope of delivery

Brand 
Woehner or equivalent

Арт.
33336000