Text for specification

Описание 
CAPUS®Panel
Выключатель-разъединитель нагрузки с предохранителями 3-полюсный
Винт M10, ручка красная
Типоразмер 1

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Сертификация
IEC (CB)

Электрические данные
Номинальный ток (IEC):	250 A
номинальное напряжение (IEC) AC:	690 В

AC-23B (690V)
AC-22B (690V)
AC-21B (690V)

рассеиваемая мощность при номинальном непрерывном токе устройства:	45,0 Вт

номинальное напряжение изоляции U  i  AC:	1000 В
номинальное импульсное напряжение U  imp :	8 kV

Mechanical lifespan (switching operations) 7000

conv. therm. current in housing
250 A, horizontal installation (adjacent poles) encapsulated 504 x 378 x 302mm
250 A, vertical installation (poles beneath each other) encapsulated 500 x 500 x 300mm

Shock protection at front with terminal space cover IP20

for fuse links DIN 43620 size 1 up to 23W power dissipation

Особенности клеммной техники
screw M10 :
Md 25 - 31 Nm

Miscellaneous 
double-breaking main contacts,
visible separation sections,
user-independent switching,
voltage-free exchange of fuses
assembly and connection material contained in scope of delivery.

Brand 
Woehner or equivalent

Арт.
33360000