Text for specification

Описание 
QUADRON^®60Classic
Держатель предохранителей Class J для установки на шины, подсоединение сверху / снизу
Для предохранителей Class J 110 - 200 A (41x146)
3-полюсный, рамная клемма
60Classic

Стандарты
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system H

Сертификация
UL

Электрические данные

номинальный ток (UL):	200 A
номинальное напряжение (UL) AC:	600 В
номинальное напряжение (UL) DC:	600 В

рассеиваемая мощность при номинальном непрерывном токе устройства:	22,3 Вт

SCCR:	200 кА

do not use any fuse links with sharp-edged contact blades

System component: degree of protection IP30 at front as per DIN EN 60529, degree of protection near terminal depends on installation
adapter module: front side degree of protection IP20 as per DIN EN 60529 (finger-safe)

Особенности клеммной техники
AWG 2 - MCM 300 stranded, equivalent to 33,6 - 152mm²

Свойства материала
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Adapter plate:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Handle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free

Miscellaneous 
the product is based on the UL approval in category IZLT2 also listed in category NMTR (file E123577)

CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom; the parts under voltage remain shock protected Simple and safe clicking into place and making contact
Safe connection through shock protection split into 2
Busbar supports for flat busbars can be mounted above each other

Brand 
Woehner or equivalent

Арт.
33403000