Text for specification

Описание 
QUADRON^®185Power
Линейный держатель NH предохранителей, 160 A
Винт М8, низкая версия
Типоразмер 00, открытая версия
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Стандарты
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Электрические данные
Номинальный ток (IEC):	160 A
номинальное напряжение (IEC) AC:	690 В
номинальное импульсное напряжение U  _imp :	12 kV
макс. напряжение IEC AC:	1000 В
устойчивость к короткому замыканию при защите предохранителями:	50 кА

Особенности клеммной техники
screw M8 : 
Md 12 - 14 Nm

Свойства материала
Main body:
	temperature stability 130°C,
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 
Shock protection cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Connecting screws:
	screw M8, galvanized, chromized 

Brand 
Woehner or equivalent

Арт.
33705000A