Text for specification

Описание 
Универсальный шинодержатель
 
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Стандарты
IEC 61439-1:2020

Сертификация
UL

Электрические данные
номинальное напряжение (IEC) AC:	800 В
номинальное напряжение (UL) AC:	1000 В
номинальное напряжение (UL) DC:	1000 В

номинальное напряжение изоляции U  i  AC:	1000 В
номинальное импульсное напряжение U  imp :	8 kV
макс. напряжение IEC DC:	1500 В

номинальный выдерживаемый пиковый ток I  pk  макс.:	106 кА

short-circuit capacity IEC / EN :
Ipk max. = 106 kA (busbars 120x10, 2 busbar supports in 550 mm distance)
go to calculation for  3-pole system (IEC) 

Brand 
Woehner or equivalent

Арт.
01430000A