Text for specification

Описание 
AMBUS^®Panel
Держатель цилиндрических предохранителей, для полупроводниковых предохранителей
22 x 58 / 2P
100 A / 690 V

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Сертификация
IEC (CB), CSA, UL, CCC

Электрические данные
Номинальный ток (IEC):	100 A
номинальное напряжение (IEC) AC:	690 В

номинальный ток (UL):	80 A
номинальное напряжение (UL) AC:	600 В
номинальное напряжение (UL) DC:	600 В

рассеиваемая мощность при номинальном непрерывном токе устройства:	7,0 Вт

номинальное напряжение изоляции U  _i  AC:	800 В
номинальное импульсное напряжение U  _imp :	6 kV

SCCR:	100 кА

for fuse links as per IEC / EN 60269-2 with permitted rated power dissipationsup to max. 9.5W for gG/gL up to max. 7W for aMfor fuse links aR / gR / gRL under operating conditions up to max. 11W, for which at least 50mm² leads must be connected

Особенности клеммной техники
box terminal :
4 - 50 mm² / AWG 10 - AWG 1/0 
flexible cables, directly or with wire-end ferrule
Md 3,5 - 4,0 Nm / 31 - 35 lb.in.

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Miscellaneous 
large clamping range

Brand 
Woehner or equivalent

Арт.
31282000