Text for specification

Описание 
QUADRON®60Classic Speed
Выключатель-разъединитель нагрузки с предохранителями 3-полюсный
Винт М10, подсоединение снизу
Типоразмер 1
60Classic

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Сертификация
IEC (CB), VDE

Электрические данные
Номинальный ток (IEC):	250 A
номинальное напряжение (IEC) AC:	690 В

AC-23B (690V/250A)
AC-23A (500V/250A)
AC-22A (690V/250A)

рассеиваемая мощность при номинальном непрерывном токе устройства:	82,0 Вт

номинальное напряжение изоляции U  i  AC:	800 В
номинальное импульсное напряжение U  imp :	8 kV

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

When several devices are used side-by-side in continuous operation, the rated load factor specified in VDE 0660 Part 500 / EN 60 439-1, Table 1, must be observed.

System component: degree of protection IP20 at front as per DIN EN 60529, degree of protection near terminal depends on installation; shock protection as per DIN EN 50274

adapter module: front side degree of protection IP20 as per DIN EN 60529 (finger-safe)

Miscellaneous 
With spring-controlled switch mechanism for frequent switching as per utilisation category &quot;A&quot;
Can be locked in neutral position with up to 3 padlocks
FLAG indicator shows the switch setting
Fuses can be changed safely and without tools thanks to double-breaking main contacts
Additional visible separating section by removing the cover incl. fuses
Can be used as mains disconnector as per IEC / EN 60204-1 (main switch).

CrossLink® adapter technology
Simple and safe clicking into place and making contact
Busbar supports can be mounted above each other for flat rails

Brand 
Woehner or equivalent

Арт.
33510000