Text for specification

Описание 
QUADRON®Panel Speed
Выключатель-разъединитель нагрузки с предохранителями 3-полюсный
Винт M10
Типоразмер 1

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Сертификация
VDE

Электрические данные
Номинальный ток (IEC):	250 A
номинальное напряжение (IEC) AC:	690 В

AC-23B (690V/250A)
AC-23A (500V/250A)
AC-22A (690V/250A)

рассеиваемая мощность при номинальном непрерывном токе устройства:	60,8 Вт

номинальное напряжение изоляции U  i  AC:	800 В
номинальное импульсное напряжение U  imp :	8 kV

Fuses gL/gG, size 1, 690V/250A for fuse links IEC 60269-2 / DIN VDE 0636-2 size 1 up to 23W power dissipation

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

When several devices are used side-by-side in continuous operation, the rated load factor specified in VDE 0660 Part 500 / EN 60 439-1, Table 1, must be observed.

System component: degree of protection IP20 at front as per DIN EN 60529, dependent upon installation in the connection area; shock protection to DIN EN 50274

Miscellaneous 
With spring-controlled switch mechanism for frequent switching as per utilisation category &quot;A&quot;
Can be locked in neutral position with up to 3 padlocks
FLAG indicator shows the switch setting
Fuses can be changed safely and without tools thanks to double-breaking main contacts
Additional visible separating section by removing the cover incl. fuses
Can be used as a mains disconnector as per IEC/EN 60204-1 (main switch function)

Brand 
Woehner or equivalent

Арт.
33512000