Text for specification

Описание 
QUADRON®185Power
модуль 4x предохранитель-разъединитель NH, 3-полюсный
4x NH 000 (max. 63 A)
185Power

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Электрические данные
Номинальный ток (IEC):	252 A
номинальное напряжение (IEC) AC:	690 В
номинальное напряжение (IEC) DC:	440 В

AC-21B (690 V / 80 A)
AC-22B (400 V / 125 A)

рассеиваемая мощность при номинальном непрерывном токе устройства:	103,0 Вт

номинальное напряжение изоляции U  i  AC:	800 В
номинальное импульсное напряжение U  imp :	6 kV

The following current capacities have been verified by tests:

with fuses 63 A / 500 V (AC): 4x 63 A
with fuses 80 A / 690 V (AC): 4x 68 A

Особенности клеммной техники
tunnel terminal 1.5 - 50 mm²

Cu: 1.5 - 50 mm² flexible with wire-end ferrule
Cu: 16 - 50 mm² stranded round
Cu: 1.5 - 10 mm² solid round

Al: 16 - 50 mm² solid round
Al: 50 mm² stranded sectored, pre-rounded 

Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

Brand 
Woehner or equivalent

Арт.
33777000A