Text for specification

Описание 
AMBUS®Panel
Держатель цилиндрических предохранителей
10 x 38 / 1P + N
32 A / 690 V

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Сертификация
IEC (CB), CSA, UL, CCC

Электрические данные
Номинальный ток (IEC):	32 A
номинальное напряжение (IEC) AC:	690 В

номинальный ток (UL):	30 A
номинальное напряжение (UL) AC:	600 В
номинальное напряжение (UL) DC:	600 В

AC-22B (400V)

рассеиваемая мощность при номинальном непрерывном токе устройства:	0,9 Вт

номинальное напряжение изоляции U  i  AC:	800 В
номинальное импульсное напряжение U  imp :	6 kV

SCCR:	100 кА

for fuse links as per IEC / EN 60269-2 with permitted rated power dissipations
up to max. 3W for gG/gL 
up to max. 1.2W for aM

Особенности клеммной техники
for applications acc. to IEC / EN :
1 wire: 
Cu 0,75 - 25 mm²
2 wires (of same cross-section): 
Cu 0,75 - 10 mm² 
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)
Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

for applications acc. to UL / CSA :
only Cu cables acc. to UL 486E
1 wire: 
AWG 18 - AWG 8, Class B, Md 2,0 -2,5 Nm / 18 - 22 lb.in.
AWG 6 - AWG 4, Class C, Md 2,5 - 3,0 Nm / 22 - 26 lb.in.
2 wires (of identical cross-section): 
AWG 18 - AWG 8, Class B, Md 2,0 - 2,5 Nm / 18 - 22 lb.in. 
AWG 6, Class C, Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

Свойства материала
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Fuse-carrier:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
	
Connecting screws:
	screw +/- (PZ2), galvanized, chromized 

Miscellaneous 
large clamping range
holder for label

Brand 
Woehner or equivalent

Арт.
31111000