Text for specification

Описание 
Шинодержатель
3-полюсный, со встроенными клеммами 1,5 - 16 мм²
60Classic

Стандарты
IEC 61439-1:2011

Электрические данные
Номинальный ток (IEC):	63 A
номинальное напряжение (IEC) AC:	690 В

рассеиваемая мощность при номинальном непрерывном токе устройства:	0,8 Вт
токовая нагрузка (IEC) макс.:	80 A

номинальное напряжение изоляции U  i  AC:	800 В
номинальное импульсное напряжение U  imp :	6 kV

Current capacity of the clamping point 80A
short-circuit withstand rating:
surge current strength &gt; 30kA at busbar support separation of 550mm
surge current strength &gt; 50kA at busbar support separation of 250mm
further values in the short-circuit withstand rating diagram

Свойства материала
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Screws:
	screw +/- (PZ2), galvanized, chromized 
Handle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94,
	creepage resistance CTI 600

Miscellaneous 
Connection busbar support with integrated terminals for feeding or tapping the busbar
with internal screw holes, can also be used as centre support.

Brand 
Woehner or equivalent

Арт.
01484000