Text for specification

Описание 
CRITO®30Compact
Соединительный модуль
С встроенными пружинными клеммами 1,5 - 16 мм², AWG 14 - 6 
3-полюсный
30Compact 3P

Стандарты
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Сертификация
UL

Электрические данные
Номинальный ток (IEC):	63 A
номинальное напряжение (IEC) AC:	690 В

номинальный ток (UL):	48 A
номинальное напряжение (UL) AC:	600 В
токовая нагрузка (IEC) макс.:	80 A

номинальное напряжение изоляции U  i  AC:	800 В
макс. напряжение IEC AC:	800 В
макс. напряжение IEC DC:	800 В

номинальный выдерживаемый пиковый ток I  pk  макс.:	10 кА

SCCR: 50 kA with JDDZ fuse Class J 60 A / 600 V AC, 35 kA with any DIVQ/7 circuit breaker 60 A / 480 V AC  

Особенности клеммной техники
for leads as per IEC :
Cu 1.5 - 16mm²
round conductor solid or stranded, flexible, direct or with wire-end ferrule

for leads as per UL :
Cu AWG 16 - 6
Class B (UL486E)

Свойства материала
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Handle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Brand 
Woehner or equivalent

Арт.
01562000A