Text for specification

Описание 
CRITO^®CrossBoard
Соединительный модуль
Хомут 150 мм²
3-полюсный

Стандарты
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Сертификация
UL

Электрические данные
Номинальный ток (IEC):	160 A
номинальное напряжение (IEC) AC:	690 В

номинальный ток (UL):	160 A
номинальное напряжение (UL) AC:	600 В
токовая нагрузка (IEC) макс.:	160 A

номинальное напряжение изоляции U  _i  AC:	800 В
номинальное импульсное напряжение U  _imp :	6 kV
макс. напряжение IEC AC:	800 В
макс. напряжение IEC DC:	800 В

номинальный выдерживаемый пиковый ток I  _pk  макс.:	30 кА

SCCR: 65 kA with any DIVQ/7 circuit breaker 400 A / 480 V AC, 100 kA with JDDZ fuse Class J 400 A / 600 V AC 

Особенности клеммной техники
Connecting circular conductors: 

35... 50 mm² / 2... 1/0 AWG 

4Nm / 35 lb in

70... 150 mm² / 2/0 AWG... 300 kcmil

6Nm / 53 lb in

35... 95 mm² flexible conductors, circular stranded conductors, flexible conductors with wire-end ferrules DIN 46228-1 max. 30 mm

120... 150 mm² flexible and circular stranded conductors

Connecting flexible conductors:

4x - 10x 15,5mm  x 0,8 mm

6Nm / 53 lb in  

Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

Brand 
Woehner or equivalent

Арт.
01595000A