Text for specification

Описание 
QUADRON®Panel
Держатель цилиндрических предохранителей
Class J / 3 полюса, клемма 70 мм²
100 A / 600 V (29 x 118)

Стандарты
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system H

Сертификация
CSA, UL

Электрические данные

номинальный ток (UL):	100 A
номинальное напряжение (UL) AC:	600 В
номинальное напряжение (UL) DC:	600 В

рассеиваемая мощность при номинальном непрерывном токе устройства:	2,5 Вт

SCCR:	200 кА

for Class J fuses 70 - 100A as per UL 248-8 (29x118)

Особенности клеммной техники
tunnel terminal with hole of 12,5 mm diameter acc. to IEC / EN :
6 - 70 mm²
flexible cables, directly or with wire-end ferrule, 
solid and stranded round cables, 
Md 14 - 16 Nm

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

acc. to UL :
AWG 10 - AWG 2/0
stranded cables Class B acc. to UL 486E
125 - 142 lb.in. 

Свойства материала
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Shock protection cover:
	temperature stability 125°C,
	fire behaviour UL 94 HB,
	creepage resistance CTI 200,
	halogen-free 

Brand 
Woehner or equivalent

Арт.
33306000