Text for specification

Описание 
QUADRON^®60Classic
Держатель предохранителей Class J для установки на шины, подсоединение сверху / снизу
Для предохранителей Class J 225 - 400 A (54x181)
3-полюсный, рамная клемма
60Classic

Стандарты
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system H

Сертификация
CSA, UL

Электрические данные

номинальный ток (UL):	400 A
номинальное напряжение (UL) AC:	600 В
номинальное напряжение (UL) DC:	600 В

рассеиваемая мощность при номинальном непрерывном токе устройства:	46,8 Вт

SCCR:	65 кА

Особенности клеммной техники
tunnel terminal with hole of 23,0 mm diameter

acc. to IEC / EN :
16 - 240 (300) mm²
flexible cables, directly or with wire-end ferrule, 
solid and stranded round cables, 
Md 38 - 40 Nm

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

acc. to UL :
AWG 4 - MCM 600
stranded cables Class B acc. to UL 486E
336 - 355 lb.in.

Свойства материала
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Shock protection cover:
	temperature stability 125°C,
	fire behaviour UL 94 HB,
	creepage resistance CTI 200,
	halogen-free 
Connecting screws:
	screw M12, galvanized, chromized

Miscellaneous 
the product is based on the UL approval in category IZLT2 also listed in category NMTR (file E123577)

Brand 
Woehner or equivalent

Арт.
33311000