Text for specification

Описание 
AMBUS®Panel
Держатель цилиндрических предохранителей, с LED
Class CC / 3P
30 A / 600 В

Стандарты
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system J

Сертификация
CSA, UL, CCC

Электрические данные

номинальный ток (UL):	30 A
номинальное напряжение (UL) AC:	600 В
номинальное напряжение (UL) DC:	600 В

рассеиваемая мощность при номинальном непрерывном токе устройства:	0,9 Вт

SCCR:	200 кА

indicator light
operating voltage range: 110 - 600 V AC / DC

Особенности клеммной техники
for applications acc. to IEC / EN :
1 wire : 
Cu 0,75 - 25 mm²
2 wires (of same cross-section) :
Cu 0,75 - 10 mm² 
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)
Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

for applications acc. to UL / CSA :
only Cu cables acc. to UL 486E 60°C/75°C
1 wire : 
AWG 18 - AWG 8, Class B, Md 2,0 -2,5 Nm / 18 - 22 lb.in.
AWG 6 - AWG 4, Class C, Md 2,5 - 3,0 Nm / 22 - 26 lb.in.
2 wires (of identical cross-section) : 
AWG 18 - AWG 8, Class B, Md 2,0 - 2,5 Nm / 18 - 22 lb.in. 
AWG 6, Class C, Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

Miscellaneous 
large clamping range, also for two identical conductors (adjacent)
holder for label
with indicator for tripped fuse
any polarity for DC voltage

Brand 
Woehner or equivalent

Арт.
31300000