Text for specification

Описание 
SECUR®Panel
Держатель цилиндрических предохранителей
10 x 85 / 1P
32 A, 1500 V DC

Стандарты
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016

Сертификация
UL

Электрические данные
Номинальный ток (IEC):	32 A
номинальное напряжение (IEC) AC:	1000 В
номинальное напряжение (IEC) DC:	1500 В

номинальный ток (UL):	30 A
номинальное напряжение (UL) DC:	1500 В

рассеиваемая мощность при номинальном непрерывном токе устройства:	0,3 Вт
номинальное импульсное напряжение U  imp :	8 kV

SCCR:	15 кА

for fuse links 10x85 or 14x85 as per IEC 60269-2, -4, -6
with permitted rated power dissipations up to max. 6.0W

Особенности клеммной техники
Box terminal

for applications acc. to IEC / EN :
1 wire: 
Cu 0,75 - 25 mm²
2 wires (of same cross-section): 
Cu 0,75 - 10 mm² 
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)
Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

for applications acc. to UL  :
only stranded Cu cables acc. to UL 486E
1 wire: 
AWG 18 - AWG 4
2 wires (of identical cross-section): 
AWG 18 - AWG 6
Md 2,0 - 2,5 Nm / 18 - 22 lb.in.

Miscellaneous 
easy replacement of the fuse-link
front degree of protection IP20 always guaranteed

Brand 
Woehner or equivalent

Арт.
31555000