Text for specification

Описание 
CAPUS^®Panel
выключатель-разъединитель нагрузки 3-полюсный
Винт M10, ручка красная
250 A

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Сертификация
IEC (CB)

Электрические данные
Номинальный ток (IEC):	250 A
номинальное напряжение (IEC) AC:	500 В

AC-23A (500A/200A)
AC-23 B (415V)
AC-22 B (500V)
AC-21 B (500V)

рассеиваемая мощность при номинальном непрерывном токе устройства:	33,5 Вт

номинальное напряжение изоляции U  _i  AC:	1000 В
номинальное импульсное напряжение U  _imp :	12 kV
номинальная включающая способность:	20 кА

conv. therm. current in housing
250 A, horizontal installation (adjacent poles) encapsulated 252 x 378 x 302mm
250 A, vertical installation (poles beneath each other) encapsulated 300 x 400 x 200 mm

max. rated operating voltage 500V AC
max. rated operating current   250A
current type AC (50-60Hz)
rated insulation voltage 1000V
rated surge voltage strength 12kV
short-time current strength   7kA -1s
rated conditional short-circuit current 80/50kA (fuses gL/gG; size 1 -200/250A-500V)
mechanical lifespan (switching operations) 7000
rated short-circuit making capacity 20kA

Особенности клеммной техники
screw M10 :
Md 25 - 31 Nm

Miscellaneous 
double-breaking main contacts, 
visible separation sections, 
user-independent switching, 
assembly and connection material contained in scope of delivery

Brand 
Woehner or equivalent

Арт.
33355000