Text for specification

Описание 
QUADRON®185Power
Линейный выключатель-разъединитель с предохранителями 630 A
Винт М12
Типоразмер 3, 1-полюсное отключение
185Power

The 185Power is an innovative busbar system for energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnectors, NH switch-disconnector-fuses and adapters for circuit breakers.

 By using Crosslink touch-safe protection modules, it is possible to build a touch-protected 185mm busbar system.

 Crosslink touch-safe protection cover with protection class IP2X front.
 Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

 All system components can be mounted safely, easily and quickly on the Crosslink touch-safe protection modules using terminal clamps.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Сертификация
IEC (CB), CCC

Электрические данные
Номинальный ток (IEC):	630 A
номинальное напряжение (IEC) AC:	690 В

AC-23B 630A/400V
AC-22B 630A/500V
AC-21B 500A/690V 

DC-20B
max. voltage between the fuses: 1000V
visible information required: Do not switch under load.

рассеиваемая мощность при номинальном непрерывном токе устройства:	118,0 Вт

номинальное напряжение изоляции U  i  AC:	1000 В
номинальное импульсное напряжение U  imp :	8 kV

Degree of protection IP20 at front, degree of protection near terminal depends on installation

Особенности клеммной техники
screw M12 :
Md 30 Nm

Miscellaneous 
Self-closing inspection holes are available in the cover.
Cover can be locked when closed.

Brand 
Woehner or equivalent

Арт.
33718000A