Text for specification

Описание 
QUADRON®60Classic
выключатель-разъединитель с предохранителями NH 000, 125 A
Рамная клемма
Подходит для 5-полюсных шинных систем
60Classic

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Электрические данные
Номинальный ток (IEC):	125 A
номинальное напряжение (IEC) AC:	690 В
номинальное напряжение (IEC) DC:	440 В

AC-21B (690 V / 80 A)
AC-22B (400 V / 125 A)

рассеиваемая мощность при номинальном непрерывном токе устройства:	10,5 Вт

номинальное напряжение изоляции U  i  AC:	800 В
номинальное импульсное напряжение U  imp :	6 kV
макс. напряжение IEC DC:	800 В

In accordance with the specified AC and DC switching properties and in consideration of the overload conditions, certain distances to earthed metal parts are to be adhered to. detailed information upon inquiry

When several devices are used side-by-side in continuous operation, the rated load factor specified in IEC / EN 61439-1, Table 1, must be observed.

Особенности клеммной техники
box terminal:
1.5 - 50 mm² flexible and flexible with wire-end ferrules*
2.5 - 50 mm² flexible
2.5 - 16 mm² solid round
2.5 - 50 mm² stranded round

Terminal space 10 mm x 10 mm

(*flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Miscellaneous 
only 49.5 mm wide rotatable for connection at bottom or top 

Brand 
Woehner or equivalent

Арт.
33803000A