Text for specification

Описание 
MOTUS®60Classic
Гибридный пускатель двигателя
0,18 - 2,4 A прямой и реверсивный пускатель / для резистивных нагрузок 0,18 - 2,4 A
60Classic

Стандарты
EN 60947-1:2015
EN 60947-4-2:2012
EN 61439-1:2012
EN 50581:2012
EN ISO 13849-1:2015

Сертификация
UL, CCC

Электрические данные
Номинальный ток (IEC):	2,4 A
номинальное напряжение (IEC) AC:	500 В

номинальный ток (UL):	2 A
номинальное напряжение (UL) AC:	500 В

рассеиваемая мощность при номинальном непрерывном токе устройства:	5,5 Вт

номинальное напряжение изоляции U  i  AC:	500 В
номинальное импульсное напряжение U  imp :	6 kV

SCCR: 100 kA with JDDZ fuse Class J 400 A / 600 V AC  

Особенности клеммной техники
Screw terminals (solid round, flexible, flexible with wire-end ferrule) 
0.14 - 2.5mm² / 0.5 - 0.6Nm
The cable outlet is provided with a pluggable terminal

Miscellaneous 
4 functions integrated:
Right contactor
Left contactor
Motor protection relay
EMERGENCY STOP protection up to category 3

Installed width only 22.5mm
30 million electrical switching operations

Brand 
Woehner or equivalent

Арт.
36105000B