Text for specification

Описание 
CRITO^®60Classic
Подсоединительная клеммная платформа, 3-полюсная
10 - 120 mm², AWG 6 - 250 MCM, lam. Cu. 9 - 15.5 x 2,4 - 10
60Classic

Стандарты
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Сертификация
CSA, UL

Электрические данные
Номинальный ток (IEC):	250 A
номинальное напряжение (IEC) AC:	690 В

номинальный ток (UL):	250 A
номинальное напряжение (UL) AC:	600 В

рассеиваемая мощность при номинальном непрерывном токе устройства:	6,0 Вт
токовая нагрузка (IEC) макс.:	440 A
номинальное импульсное напряжение U  _imp :	6 kV
макс. напряжение IEC AC:	1000 В
макс. напряжение IEC DC:	1500 В

номинальный выдерживаемый пиковый ток I  _pk  макс.:	56,3 кА

SCCR: 35 kA with any DIVQ/7 circuit breaker 600 A / 600 V AC, 50 kA with any DIVQ/7 circuit breaker 600 A / 480 V AC, 100 kA with JDDZ fuse Class J 600 A / 480 V AC, 100 kA with JDDZ fuse Class J 500 A / 600 V AC, 65 kA with any DIVQ/7 circuit breaker 400 A / 480 V AC 

Особенности клеммной техники
16 - 120 mm² / AWG 6 - 250 MCM flexible cables, directly
10 - 120 mm² / AWG 7 - 250 MCM flexible cables with wire-end ferrule
16 - 150 mm² / AWG 6 - 300 MCM stranded round cables
10 mm² rigid cables
lam. Cu 12x4 - 15,5x10
Md 12 - 12,5 Nm / 106 lb-in

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Свойства материала
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free

Miscellaneous 
Terminals can be removed for connection of uncut conductors

Brand 
Woehner or equivalent

Арт.
01243000