Text for specification

Описание 
CRITO^®
Цанговая клемма
Cu / Al 95 - 185 mm²
60Classic
100Energy
185mm-System
Центральный ввод питания

Стандарты
IEC 61439-1:2011
IEC 60999-1:1999
IEC 60999-2:2003

Сертификация
UL

Электрические данные
Номинальный ток (IEC):	300 A
номинальное напряжение (IEC) AC:	690 В

номинальный ток (UL):	310 A
номинальное напряжение (UL) AC:	600 В
токовая нагрузка (IEC) макс.:	500 A
макс. напряжение IEC AC:	1000 В
макс. напряжение IEC DC:	1500 В

номинальный выдерживаемый пиковый ток I  _pk  макс.:	55,8 кА

SCCR:	25 кА

Особенности клеммной техники
for applications acc. to IEC / EN :
Cu or Al 95 - 185 mm² stranded round cables and stranded sectored cables
Cu also flexible cables, directly,

for applications acc. to UL / CSA :
Cu 95 - 185 mm² / AWG 3/0 - MCM 350
Suitable for aluminium cables.
When using aluminium cables, observe the maintenance instructions.

Свойства материала
Connecting screws:
	Set screw M16, Allan key size 8
Terminal body:
	steel, galvanized and chromized
cable base:
	brass, tin plated

Terminal body: 	galvanised steel, chromited screw: 	hexagonal socket screw M16 x 1.5 (S8), galvanised, chromited, cable bed: 	brass, nickel-plated

Miscellaneous 
Terminal with captive clamp screws, conductor can be overlapped, indication of nominal cross-section and tightening torque noted on the terminal, contact between conductor and busbar via cable bed.

Brand 
Woehner or equivalent

Арт.
01318000