Text for specification

Описание 
SECUR®Panel
Выключатель-разъединитель для D0-предохранителей до 63 А
С LED
3-полюсный

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Сертификация
VDE

Электрические данные
Номинальный ток (IEC):	63 A
номинальное напряжение (IEC) AC:	400 В
номинальное напряжение (IEC) DC:	130 В

AC-22B

рассеиваемая мощность при номинальном непрерывном токе устройства:	7,8 Вт

номинальное напряжение изоляции U  i  AC:	500 В
номинальное импульсное напряжение U  imp :	6 kV

for fuse links and gauge rings as per DIN VDE 0636-3 IEC / HD 60269-3
utilisation category as per VDE 0638 : AC-22

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard.

There is a transfer of the potential from the busbars, through the LED units, to the terminals  when the fuse links are removed and the switching mechanismn is closed. 

Особенности клеммной техники
box terminal :
1,5 - 35 mm²    flexible cables, directly or with wire-end ferrule
(flexible cables of maximum cross-section may not fit when using wire-end ferrule)
1,5 - 10 mm²    solid
Md 2,5 - 3 Nm

2 cables can be connected, when both chambers of the terminal are used
the maximum combination is 35mm² + 16mm²

Свойства материала
Body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Handle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
	
Fuse-carrier:
	temperature stability 150°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 125,
	halogen-free
Connecting screws:
	screw +/- (PZ2), galvanized, chromized 

Miscellaneous 
Double function terminal
any feed direction
captive fuse-carrier
sealable operation

Brand 
Woehner or equivalent

Арт.
31557000A