Text for specification

Описание 
SECUR®60Classic EasyLiner
Выключатель-разъединитель с D0-предохранителями для установки на шины 3 полюсов
Для D01 и D02 предохранителей, с LED
E18 / 63 A / 3 полюса
60Classic

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Сертификация
IEC (CB), VDE, CCC

Электрические данные
Номинальный ток (IEC):	63 A
номинальное напряжение (IEC) AC:	400 В

AC-22B (400 В)

рассеиваемая мощность при номинальном непрерывном токе устройства:	7,0 Вт

номинальное напряжение изоляции U  i  AC:	500 В
номинальное импульсное напряжение U  imp :	6 kV

reduction factor at ambient temperature:
 35°C     1,0
 45°C     0,9
 55°C     0,8

for fuse links and gauge elements acc. to IEC / HD 60269-3

 use of D02 fuse links with silver plated caps is recommended

The function of isolation between incoming and outgoing contacts is provided by the opening of the switching mechanism as required in the standard.

There is a transfer of the potential from the busbars, through the LED units, to the terminals  when the fuse links are removed and the switching mechanismn is closed. 

Особенности клеммной техники
1,5 - 16 mm² round stranded and flexible without wire-end ferrule
1,5 - 16 mm²  flexible with wire-end ferrule*
1,5 - 10 mm²  flexible with wire-end ferrule
1,5 - 10 mm² round solid

* 16 mm² prepared with crimping tool PZ 16 (Weidmüller) or
with jointing clamp Crimpfox 25R (Phoenix Contact)

the connecting wires can be placed at the side :
up to 6mm² without side module
up to 10mm² when using  the side module

Свойства материала
Body:
	temperature stability 130°C,
	self-extinguishing in acc. to UL 94,
	creepage resistance CTI 600,
	halogen-free 
Handle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
spring terminal enables connection without tools (at first installation)

Brand 
Woehner or equivalent

Арт.
31575000B