Text for specification

Описание 
QUADRON®Panel
Выключатель-разъединитель с предохранителями NH типоразмер 3, 630 A, панельный монтаж
Винт М12

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Сертификация
IEC (CB), UL, CCC

Электрические данные
Номинальный ток (IEC):	630 A
номинальное напряжение (IEC) AC:	690 В
номинальное напряжение (IEC) DC:	440 В

номинальный ток (UL):	600 A
номинальное напряжение (UL) AC:	600 В

AC-23B (400V)
AC-22B (690V)
AC-21B (690V)
AC-20B (1000V) at pollution degree 2

visible information required if used at more than 690V AC: do not switch under load

DC specifications: 2 current paths (L1,L3) in series
DC-22B (440V)
DC-21B (440V)
DC-20B (1000V) at pollution degree 2

visible information required if used at more than 440V DC: do not switch under load

рассеиваемая мощность при номинальном непрерывном токе устройства:	36,0 Вт

номинальное напряжение изоляции U  i  AC:	800 В
номинальное импульсное напряжение U  imp :	6 kV
макс. напряжение IEC DC:	800 В

номинальный выдерживаемый пиковый ток I  pk  макс.:	35,2 кА

SCCR:	100 кА

Entsprechend den angegeben AC- und DC- Schalteigenschaften und unter Berücksichtigung der Überlastbedingungen, sind gewisse Abstände zu geerdeten Metallteilen einzuhalten. Nähere Informationen auf Anfrage.
Bei Verwendung als Trennschalter ist die Einhaltung der Abstände nicht erforderlich.

Degree of protection IP30 at front, degree of protection near terminal depends on installation

Особенности клеммной техники
Accessories:
Clamp connection:  Cu 150-300mm² s(r), f+AE; lam. Cu 25x1-13; 6-8Nm torque
single wedge clamp terminal: Cu, Al* 150-300mm² s(r), s(s), f, f+AE; 6-8 Nm torque
double wedge clamp terminal: Cu  2x 150-185mm² s(r), s(s), f+AE;  6-8Nm torque

*Connections are not maintenance-free if aluminium conductors are used.

Свойства материала
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Shock protection cover:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200
Handle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 200,
	halogen-free
Contacts:
	spring-loaded copper contacts, silver plated 

Miscellaneous 
Disconnectors are equipped with arc chambers.
The shock protection is split into 2 for safe connection of the conductors.
Self-closing inspection holes, which can be punched out, are available in the cover.

Brand 
Woehner or equivalent

Арт.
33203000