Text for specification

Описание 
CAPUS®Panel
Выключатель-разъединитель нагрузки с предохранителями 3-полюсный
Винт M8, ручка серая
Типоразмер 00

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Сертификация
IEC (CB)

Электрические данные
Номинальный ток (IEC):	160 A
номинальное напряжение (IEC) AC:	690 В

AC-23A (690V/125A)
AC-23A (500V)
AC-22A (690V)
AC-21A (690V)

рассеиваемая мощность при номинальном непрерывном токе устройства:	28,0 Вт

номинальное напряжение изоляции U  i  AC:	1000 В
номинальное импульсное напряжение U  imp :	8 kV

Mechanical lifespan (switching operations) 7000

conv. therm. current in housing
160 A, horizontal installation (adjacent poles) encapsulated 252 x 378 x 302mm
145 A, vertical installation (poles beneath each other) encapsulated 500 x 500 x 300mm

Shock protection at front with terminal space cover IP20

for fuse links DIN 43620 size 00 up to 12W power dissipation

Особенности клеммной техники
screw M8 :
Md 12,5 - 15,5 Nm

Miscellaneous 
double-breaking main contacts,
visible separation sections,
user-independent switching,
voltage-free exchange of fuses
assembly and connection material contained in scope of delivery.

Brand 
Woehner or equivalent

Арт.
33337000