Text for specification

Описание 
CAPUS®Panel
выключатель-разъединитель нагрузки 3-полюсный
Винт M10, ручка красная
630 A

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Сертификация
IEC (CB)

Электрические данные
Номинальный ток (IEC):	630 A
номинальное напряжение (IEC) AC:	500 В

AC-23B (500V)
AC-22B (500V)
AC-21B (500V)

рассеиваемая мощность при номинальном непрерывном токе устройства:	127,0 Вт

номинальное напряжение изоляции U  i  AC:	1000 В
номинальное импульсное напряжение U  imp :	12 kV
номинальная включающая способность:	30 кА

Switching capacity/utilisation categories AC-23B (500V);  AC-22B (500V); AC-21B (500V)
Mechanical lifespan (switching operations) 7000
Rated short-circuit making capacity 30kA

conv. therm. current in housing
630 A, horizontal installation (adjacent poles) encapsulated 504 x 378 x 302 mm
630 A, vertical installation (poles beneath each other) encapsulated 500 x 500 x 300 mm

Shock protection at front with terminal space cover IP40

Особенности клеммной техники
screw M10 :
Md 25 - 31 Nm

Miscellaneous 
double-breaking main contacts, 
visible separation sections, 
user-independent switching, 
assembly and connection material contained in scope of delivery

Brand 
Woehner or equivalent

Арт.
33357000