Text for specification

Описание 
QUADRON®60Classic Speed
выключатель-разъединитель нагрузки 3-полюсный
Рамная клемма, подсоединение сверху, для соединения с поворотной рукояткой двери
160 A
60Classic

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Электрические данные
Номинальный ток (IEC):	160 A
номинальное напряжение (IEC) AC:	690 В

AC-23B (690V/125A)
AC-23A (500V/125A)
AC-22A (690V/160A)

2 current paths (L1,L3) in series
DC-22B (220V/125A)

номинальное напряжение изоляции U  i  AC:	800 В
номинальное импульсное напряжение U  imp :	8 kV

rated short-circuit making capacity 7kA (690V AC) cond. rated short-circuit current 50kA (fuses gL/gG size 00 125A-690V AC) utilisation categories AC-23B (690V/125A), AC-23A (500V/125A), AC-22A (690V/160A) DC-22B (220V/125A), 2 current paths (L1,L3) in series;

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

When several devices are used side-by-side in continuous operation, the rated load factor specified in VDE 0660 Part 500 / EN 60 439-1, Table 1, must be observed.

System component: degree of protection IP20 at front as per DIN EN 60529, degree of protection near terminal depends on installation; shock protection as per DIN EN 50274
adapter module: front side degree of protection IP20 as per DIN EN 60529 (finger-safe)

Особенности клеммной техники
Box terminal:
1.5 -70mm² flexible cables, directly or with wire-end ferrules*, depending on contour of the insulated lead 95mm² could be connectable 
1.5 - 10mm² solid round
16 - 70mm² stranded round 
2x10mm², 2x16mm² and 2x25mm² flexible with wire-end ferrules, identical cables placed side by side, crimping square 
2x10 - 2x35mm² flexible, identical cables placed side by side square

lam. Cu. 9-13 mm wide 
Terminal space 13mm x 13mm

(*flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Свойства материала
Main body:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Adapter plate:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free
Handle:
	temperature stability 125°C, 
	self-extinguishing in acc. to UL 94, 
	creepage resistance CTI 600,
	halogen-free

Miscellaneous 
With spring-controlled switch mechanism for frequent switching as per utilisation category &quot;A&quot;
Lockable in neutral position with up to 3 padlocks
FLAG indicator shows the switch setting double-breaking main contacts
Can be used as a mains disconnector as per IEC / EN 60204-1 (main switch) 
Can also be used as an Emergency Off switch in combination with the door coupling twist handle
Main switch and Emergency Off switch only in combination with AC-23A/B
AC-23B (690V/125A), AC-23A (500V/125A)

CrossLink® adapter technology
Simple and safe clicking into place and making contact
Busbar supports can be mounted above each other for flat busbars

Switches can be installed 90° left/right horizontal, always with the same switch handle position

Compact dimensions (106mm wide)

Brand 
Woehner or equivalent

Арт.
33544000