Text for specification

Описание 
AMBUS®Panel
Держатель цилиндрических предохранителей
Class J / 3 полюса, рамная клемма 50 мм²
30 A / 600 В (21x57)

Стандарты
IEC 60269-1:2006 + A1:2009 + A2:2014
IEC 60269-2:2013 + A1:2016, Fuse system H

Сертификация
CSA, UL

Электрические данные

номинальный ток (UL):	30 A
номинальное напряжение (UL) AC:	600 В
номинальное напряжение (UL) DC:	600 В

рассеиваемая мощность при номинальном непрерывном токе устройства:	0,6 Вт

SCCR:	200 кА

for Class J fuses 1 - 30A as per UL 248-8 (21x57)

Особенности клеммной техники
for applications acc. to IEC / EN :
1 wire : 
Cu 0,75 - 1,0 mm², Md 2,0 - 2,5 Nm / 18 - 22 lb.in.
Cu 1,5 - 50 mm², Md 3,5 - 4,0 Nm / 31 - 35 lb.in.
2 wires (of same cross-section) : 
Cu 0,75 - 1,0 mm², Md 2,0 - 2,5 Nm / 18 - 22 lb.in.
Cu 1,5 - 10 mm², Md 3,5 - 4,0 Nm / 31 - 35 lb.in.
flexible cables, directly or with wire-end ferrule
(flexible cables of max. cross-section may not fit when using wire-end ferrule)

for applications acc. to UL / CSA :
only Cu cables acc. to UL 486E 60°C/75°C
1 wire : 
AWG 18 - AWG 1, Class B, Md 3,5 - 4,0 Nm / 31 - 35 lb.in.
2 wires (of identical cross-section) : 
AWG 18 - AWG 8, Class B, Md 3,5 - 4,0 Nm / 31 - 35 lb.in.

Miscellaneous 
large clamping range, also for two identical conductors (adjacent)
holder for label

Brand 
Woehner or equivalent

Арт.
31287000