Text for specification

Описание 
EQUES®185Power
Шинный адаптер 1500A
300 x 652, подсоединение снизу, зажим хомутом
185Power

The 185Power is an innovative and powerful busbar system for professional energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnector, NH-switch-disconnector-fuses and adapters for circuit breakers.

Easy design of touch-safe busbar system by using Crosslink touch-safe protection covers.

Crosslink touch-safe protection cover with protection class IP2X front.
Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

Safe and fast drill-free mounting by terminal clamps of all system components on Crosslink touch-safe protection modules.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second. 

Стандарты
IEC 61439-1:2011

Сертификация
UL

Электрические данные
Номинальный ток (IEC):	1 500 A
номинальное напряжение (IEC) AC:	690 В
номинальное напряжение (IEC) DC:	800 В

номинальный ток (UL):	1 200 A
номинальное напряжение (UL) AC:	1000 В

рассеиваемая мощность при номинальном непрерывном токе устройства:	594,0 Вт

номинальное напряжение изоляции U  i  AC:	1000 В
номинальное импульсное напряжение U  imp :	12 kV

номинальный выдерживаемый пиковый ток I  pk  макс.:	106 кА

with Socomec Sirco 1250 A (Socomec no.26003U21) and 1600 A (Socomec no.26003U61) usable up to 1550 A
maximum 300 switching cycles

Brand 
Woehner or equivalent

Арт.
32764000A