Text for specification

Описание 
QUADRON^®60Classic
Выключатель-разъединитель с предохранителями NH типоразмер 1, 250 A, шинный монтаж
Рамная клемма
60Classic

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Сертификация
IEC (CB), UL, VDE, CCC

Электрические данные
Номинальный ток (IEC):	250 A
номинальное напряжение (IEC) AC:	690 В
номинальное напряжение (IEC) DC:	440 В

номинальный ток (UL):	250 A
номинальное напряжение (UL) AC:	600 В

AC-22B (400 V)
AC-23B (400 V / 160 A)
AC-21B (690 V)
AC-20B (1000 V) at pollution degree 2

to obtain a higher utilisation category the product can be retrofitted with arcing chambers (see accessories)

visible information required if used at more than 690V AC: do not switch under load

DC specifications: 2 current paths (L1,L3) in series
DC-20B (440 V)
DC-20B (1000V) at pollution degree 2

visible information required if used at more than 440V DC: do not switch under load

рассеиваемая мощность при номинальном непрерывном токе устройства:	26,0 Вт

номинальное напряжение изоляции U  _i  AC:	800 В
номинальное импульсное напряжение U  _imp :	6 kV
макс. напряжение IEC AC:	725 В
макс. напряжение IEC DC:	800 В

номинальный выдерживаемый пиковый ток I  _pk  макс.:	13,7 кА

SCCR:	100 кА

In accordance with the specified AC and DC switching properties and in consideration of the overload conditions, the distances to earthed metal parts given below are to be adhered to. - top 190mm, side 75mm
When used as a disconnector, the spacings can be ignored.

Degree of protection IP30 at front, degree of protection near terminal depends on installation

Особенности клеммной техники
box terminal

Cu 70-185mm²f
Cu 35-150mm²s(r)
Cu 35-120mm²f+AE
lam.Cu 15.5-24mm large
terminal space 24.5 x 12mm
min. terminal space heigt 3mm

(flexible cables of maximum cross-section may not fit when using wire-end ferrule)

Miscellaneous 
CrossLink® adapter technology
Fast and safe conversion of the connection for top or bottom; the parts under voltage remain shock protected
Simple and safe clicking into place and making contact
Safe connection through shock protection split into two
Busbar supports for flat busbars can be mounted above each other
Self-closing test holes are available in the cover.

Brand 
Woehner or equivalent

Арт.
33600000