Text for specification

Описание 
QUADRON®185Power
Сдвоенный линейный выключатель с предохранителями 1250 А
3-полюсное отключение
Винт M12, включая крышки для клемм
185Power

Стандарты
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

Электрические данные
Номинальный ток (IEC):	1 250 A
номинальное напряжение (IEC) AC:	690 В

AC-20B (690 V)

DC-20B
max. voltage between the fuses: 800 V
visible information required: Do not switch under load.

рассеиваемая мощность при номинальном непрерывном токе устройства:	380,0 Вт

номинальное напряжение изоляции U  i  AC:	1000 В
номинальное импульсное напряжение U  imp :	8 kV

version: connection bottom

ampacity with fuses NH3 gG 500 V AC 630 A:
- 1250 A bolt connection (it's recommended to wear gloves when operating)
- 1190 A bolt connection
- 1125 A using terminal clamp 33738 or 33740

ampacity with solid links (knives) 1000 A:
- 1550 A bolt connection
- 1350 A using terminal clamp 33738 or 33740 

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

Degree of protection IP20 at front, degree of protection near terminal depends on installation

Особенности клеммной техники
screw M12 :
Md 30 Nm

Miscellaneous 
Self-closing inspection holes are available in the cover.

Cover can be locked when closed.

Brand 
Woehner or equivalent

Арт.
33731000A