招标说明 - 计划 

说明
QUADRON^®185Power
条形熔断器式隔离开关 250 A
尺寸 1，3 极分断
螺钉 M12
185Power

185Power是具有革新意义的用于电能分配的母线系统, 包括母线系统、用于供电的连接模块/条形连接器,加长连接夹,条形NH-熔断器式隔离开关, 条形NH-隔离开关熔断器组和连接断路器的转接器

通过 Crosslink防触摸保护模块的使用实现185mm母线系统的防触摸保护。

Crosslink 防触摸保护模块的防护等级为IP2X(正面)。
Crosslink防触摸保护带有附加的缝隙盖罩IP4X(正面)

所有的系统部件可以通过挂钩安全、简便、快捷的安装在Crosslink防触摸保护模块上。

30mm,  40mm,  60mm,  80mm,  100mm,  120mm x 10mm的扁平铜母线系统。选择组装的短路稳定性已通过检测。可达到的最大值为: 脉冲峰值电流 Ipk最大105kA/秒,  Icw 最大50kA/秒。 

标准
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

认证许可
IEC (CB), CCC

电气数值
额定电流（IEC）:	250 A
额定电压（IEC）AC:	800 V

AC-23B 250A/400V
AC-22B 250A/500V
AC-22B 250A/690V
AC-21B 250A/690V

DC-20B
max. voltage between the fuses: 1000 V
visible information required: Do not switch under load.

power dissipation at full load of the item:	24.0 W

rated isolation voltage U_i AC:	1000 V
额定冲击耐受电压 U_imp:	12 kV

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

防护等级 IP20 正面(参阅安装说明)

其他
盖罩带有自动闭合的检测孔。

盖罩在关闭状态下可锁定。 

品牌
维纳尔或同等价值的产品

订货号
33574000A