招标说明

说明
QUADRON^®185Power
双条形熔断器式隔离开关 1250 A
3 极分断
螺钉 M12，含连接空间盖罩
185Power

标准
IEC 60947-1:2020
IEC 60947-3:2020 AC ratings only

电气数值
额定电流（IEC）:	1,250 A
额定电压（IEC）AC:	690 V

AC-20B (690 V)

DC-20B
max. voltage between the fuses: 800 V
visible information required: Do not switch under load.

power dissipation at full load of the item:	380.0 W

rated isolation voltage U_i AC:	1000 V
额定冲击耐受电压 U_imp:	8 kV

version: connection bottom

ampacity with fuses NH3 gG 500 V AC 630 A:
- 1250 A bolt connection (it's recommended to wear gloves when operating)
- 1190 A bolt connection
- 1125 A using terminal clamp 33738 or 33740

ampacity with solid links (knives) 1000 A:
- 1550 A bolt connection
- 1350 A using terminal clamp 33738 or 33740

Special operating conditions corresponding to IEC / EN 61439-1 may yield to foulty activations of pilot switches and fuse monitors. The operating conditions have to be considered for the analysis of status signals.

防护等级 IP20 正面, 取决于安装时的连接区域 

连接端
螺钉 M12 : 
扭力矩 30 Nm 

原材料性能
主体:
	耐温性最高 130°C, 
	根据UL 94 有阻燃性, 
	耐蠕变性 CTI 600, 
	不含卤素
触点:
	预压紧弹性铜连接, 镀银   
防触摸保护:
	耐温性最高 125°C, 
	根据UL 94 有阻燃性, 
	耐蠕变性 CTI 200, 
	不含卤素
盖罩:
	耐温性最高 125°C, 
	根据UL 94 有阻燃性, 
	耐蠕变性 CTI 200, 
	不含卤素
连接螺钉:
	螺钉 M12, 镀锌, 镀铬 

其他
盖罩带有自动闭合的检测孔。

盖罩在关闭状态下可锁定。 

品牌
维纳尔或同等价值的产品

订货号
33731000A