招标说明

说明
EQUES®185Power
母线转接器 1500A
300 x 675, 下端连接，端子连接
185Power

The 185Power is an innovative and powerful busbar system for professional energy distribution coming with busbar system, connection rails and modules as feeders, busbar connectors, NH in-line fuse-switch-disconnector, NH-switch-disconnector-fuses and adapters for circuit breakers.

Easy design of touch-safe busbar system by using Crosslink touch-safe protection covers.

Crosslink touch-safe protection cover with protection class IP2X front.
Crosslink touch-safe protection cover with additional front cover enhance protection class to IP4X front.

Safe and fast drill-free mounting by terminal clamps of all system components on Crosslink touch-safe protection modules.

The busbar system comes with copper busbars of 30mm, 40mm, 60mm, 80mm, 100mm, 120mm x 10mm. For selected application set up’s, short circuit capabilities are proven by tests. The achievable maximum ratings are rated peak withstand current Ipk max. 105kA, rated short-time withstand current Icw max. 50kA at 1 second.

标准
IEC 61439-1:2020

认证许可
UL

电气数值
额定电流（IEC）:	1,500 A
额定电压（IEC）AC:	690 V
额定电压 （IEC） DC:	800 V

额定电流 (UL):	1,200 A
额定电压 (UL) AC:	1000 V

power dissipation at full load of the item:	594.0 W

rated isolation voltage Ui AC:	1000 V
额定冲击耐受电压 Uimp:	12 kV

额定冲击耐受电流 Ipk :	106 kA

with Socomec Sirco 1250 A (Socomec no.26003U21) and 1600 A (Socomec no.26003U61) usable up to 1550 A
maximum 300 switching cycles

品牌
维纳尔或同等价值的产品

订货号
32764000A